#### GEN X- Communicating VVT SYSTEM CONTROLLER

#### SUBMITTAL

DESCRIPTION

The GEN X is a microcontroller based, auto change- over Universal Gas/Electric or Heat Pump system controller (Part # GEN X).  The GEN X controls a zoned 2H/2C Gas/Electric HVAC unit or 3H/2C zoned Heat Pump unit and supports ADR and FDD requirements and communicates with and supports up to 20 zones, utilizing pressure dependent, modulating dampers and wired or wireless thermostats.  Communications hub is APP based and accessed via mobile phone, tablets, or the internet. GEN X is native BACnet compliant allowing for seamless integration with BAS systems.

The GEN X gathers information every 60 seconds from each thermostat (EzTouchX), or damper board used with (WSTATX) while the thermostats communicate with the system over a 3-wire data link directing control-based decisions to the HVAC equipment.

The GEN X is powered with one 24V/100VA transformer, which also powers all dampers and thermostat (if wired) in the system.  Power from the controller, along with a 3-wire twisted pair communications loop, is daisy chained damper to damper with wireless thermostats or wired thermostat to wired thermostat to streamline installation and system communications.

The GEN X is equipped with integrated capacity control and High and Low temperature limits to protect compressors and heat exchanger.  Outside air and return Air sensors are also provided. The HVAC unit is staged based on leaving air temperature and time.  Auto changeover operation is vote based, predicated on a first call, first served, majority wins on changeover algorithm.

##### GEN X Wi-Fi

##### Mobile APP based VVT

##### BACnetIP

##### System Controller

The Gen X is expandable up to 20 additional RTU’s or split systems using the add-on GEN X-RM controller that is daisy chained via the (RS485) communications loop. Each

GEN X-RM supports up to 20 zones or stand-alone units to support up to 400 thermostats or zones in your system.

TECHNICAL DATA

Electrical

Supply Voltage: 24vac

Power consumption: 0.7 VA

Inputs:

24vac

3 Temperature Sensing Thermistors

Outputs:

24vac

5 SPST dry contacts, 1A @ 24vac

Fuse protection: Use Fused Transformer

BACnet Interface

Communication Protocol: BACnetIP Connection

Type: Ethernet

Wiring: 10Base-T/100Base-TX

Environmental

Operating temperature: 32 to 160° F (0 to 71° C)

Operating humidity: 10-95%, non-condensing

Storage temperature: 0 to 160° F (-18 to 71° C)

General

Communications: 3 wire Plenum rated twisted pair Zonex Wire

Enclosure Dimensions: 6 ¼” x 4 ¼ “x1”

6/29/20